## Addendum 02
Common Services electrical Installations
Ground & First and Typical floors (common areas)
B14 | Sub - mains and distribution
ITEM | DESCRIPTION | Unit | Gnd | Ty 1 | Ty 2 | Ty 3 | Ty 4 | FL 5-9 | Prayer room | Game room | Lockers gr to 4th | Custodian office | Students lounge 1 to 3 | Students lounge 1 to 4 | Qty | RATE (Kshs.) | COST (Kshs.)
B14.01 | DB CS 001 ( Main commons) 16Way 100A rated TPN SURFACE Wall mounted Distribution Board | No. | 1 | 1 | 1 | 1 | 1 | 5 | [6 empty] | 32 |  | 0
B14.02 | Cable to DB Above: 25mm sq 4-Core PVC SWA PVC XLPE CU Cable | LM | 5 | [11 empty] | 60 |  | 0
B14.03 | ► 80A 3-P MCB's - No. 5 | No. | [12 empty] | 5 |  | 0
B14.04 | COMMON SERVICES METERBOARD 01 (AMS): As per schematic drawing including the following: | No. | [12 empty] | 1 |  | 0
An appropriate 3-Phase 80kA Surge Arrestor Type Dehnventil DVTT 225 or equivalent complete with appropriate protection
A 3Phase KPLC CT metering chamber.
Termination point for connection of remote signals for: • Mains available & Mains on Load on Mains section • Generator available & Generator on Load on Generator section. • Stabilizer status on the particular section.
Panel shall also include a fireman's switch termination point ( Shunt Trip )
Panel shall comprise the following switchgear:
Main Incomer
a | Incoming breaker with adjustable overcurrent settings, Auxilary contact for breaker monitoring, having a short circuit breaking capacity of 50KA at 415Vac, 50Hz. Rating: 1000 Amps 4P MCCB Qty - 1No
b | Supply and Install a Set of digital energy multimetre (complete with current transformers and fuse holder/fuses) for indication of voltage, current, kW, kWh, KVA, power factor, etc. as PM5310 or higher
Busbars Feed Breaker
a | Supply Breakers and associated PLC, with adjustable overcurrent settings, auxilary contact for breaker monitoring, having a short circuit breaking capacity of 50KA at 415Vac, 50Hz with Shunt trip for Firemans switch Rating: 1000 Amps 4P MCCB Qty - 1No
Busbars
a | TPN rated busbars with a provision for future expansion. Rating: 500A
b | Neutral link bar and earth bar
B14.05 | COMMON SERVICES METERBOARD 02 (I H S): As per schematic drawing including the following: | No. | [12 empty] | 1 |  | 0
An appropriate 3-Phase 80kA Surge Arrestor Type Dehnventil DVTT 225 or equivalent complete with appropriate protection
A 3Phase KPLC CT metering chamber.
Termination point for connection of remote signals for: • Mains available & Mains on Load on Mains section
Panel shall also include a fireman's switch termination point ( Shunt Trip )
Panel shall comprise the following switchgear:
Main Incomer
a | Incoming breaker with adjustable overcurrent settings, Auxilary contact for breaker monitoring, having a short circuit breaking capacity of 50KA at 415Vac, 50Hz. Rating: 160 Amps 4P MCCB Qty - 1No
b | Supply and Install a Set of digital energy multimetre (complete with current transformers and fuse holder/fuses) for indication of voltage, current, kW, kWh, KVA, power factor, etc. as PM5310 or higher
Busbars Feed Breaker
a | Supply Breakers and associated PLC, with adjustable overcurrent settings, auxilary contact for breaker monitoring, having a short circuit breaking capacity of 50KA at 415Vac, 50Hz with Shunt trip for Firemans switch Rating: 160 Amps 4P MCCB Qty - 1No
Busbars
a | TPN rated busbars with a provision for future expansion. Rating: 200A
b | Neutral link bar and earth bar
B14.06 | MAIN DISTRIBUTION PANEL (AMS): As per schematic drawing including the following: | No. | [12 empty] | 1 |  | 0
An appropriate 3-Phase 80kA Surge Arrestor Type Dehnventil DVTT 225 or equivalent complete with appropriate protection
A 3Phase KPLC CT metering chamber.
Termination point for connection of remote signals for: • Mains available & Mains on Load on Mains section
Panel shall also include a fireman's switch termination point ( Shunt Trip )
Panel shall comprise the following switchgear:
Main Incomer
a | Incoming breaker with adjustable overcurrent settings, Auxilary contact for breaker monitoring, having a short circuit breaking capacity of 50KA at 415Vac, 50Hz. Rating: 1000A 3P DRAWOUT ACB Qty - 1No
b | Supply and Install a Set of digital energy multimetre (complete with current transformers and fuse holder/fuses) for indication of voltage, current, kW, kWh, KVA, power factor, etc. as PM5310 or higher
Busbars
a | TPN rated busbars with a provision for future expansion. Rating: 1000A
b | Neutral link bar and earth bar
Outgoers
a | Outgoing breaker with adjustable overcurrent settings, Auxilary contact for breaker monitoring, having a short circuit breaking capacity of 50KA at 415Vac, 50Hz. Rating: 500A 3P DRAWOUT ACB Qty - 2No
c | Outgoing breaker with adjustable overcurrent settings, Auxilary contact for breaker monitoring, having a short circuit breaking capacity of 50KA at 415Vac, 50Hz. Rating: 500A 3P MCCB Qty - 2No
d | 3-PHASE Blanked Spareways for upto 250A 3P MCCB Qty - 1No
B14.07 | Total Exclusive of VAT to electrical price summary page. | [15 empty] | 0

## Addendum 01 - Switch Gear
C | MAIN POWER DISTRIBUTION - SWITCHGEAR, RISING MAINS, EARTHING & CABLING
C1 | Switchgear |  |  |  | Total
ITEM | DESCRIPTION | UNIT | QTY | RATE (Kshs) | COST (Kshs)
C1.01 | Commons LV Board : Custom made LV Meterboard. This should be as per the schematic drawing & have the following specifications: | No. | 1 |  | 0
• As Terrasaki to Approval
• Free Standing Panel
• Form 2b Panel
• Single side view & Access
• The Meterboard should comprise of a 3-Phase 80kA Surge Arrestor Type Dehnventil DVTT 225 or equivalent complete with appropriate protection
•Verified Assembly as per IEC 61439-1&2
• The Panel to be fabricated using a minimum of 16 SWG or 2mm thick steel sheets
• Should include phase indicator LED lights & all associated instrumentation
• Should include Digital Energy Meter as PM5310 or higher.
• Panel shall include appropriate Neutral & Earth Bars
• Should contain a connector block for termination of outgoing cables.
• Should contain a Cable Chamber for running of outgoing cables.
• Meterboard shall incorporate Appropriate surge protector c/w protection
• The Main Incomer shall be:
► 1No. 1000A TP Rated MCCB (Adjustable) with Shunt trip for Firemans switch
• The outgoers shall be as follows:
► 100A 3-P MCB's - No. 3
► Neutral Terminal for MCCB's above
► Neutral Terminal for MCCB's above
• The Outgoers shall be:
a | 200A TP MCCB's for Rising Mains • Qty - 5
b | 100A TP MCCB's for Pump output • Qty - 2
c | 100A TP MCCB for Output to DBx • Qty - 1
100A 3-P MCB • Qty - 3
d | 3-PHASE Blanked Spareways for upto 63A 3P MCCB • Qty - 2
► Neutral Terminal for MCCB's above
► Neutral Terminal for MCCB's above
C1.02 | Taking delivery on site, Positioning, termination, and testing and commissioning Commons LV Board described above. | Item | 1 |  | 0
C1.03 | LABELLING (Internal & External): Labelling of Panels with permanent Engraved labels of Visible Font. Engraved plate shall be Grey in Colour with white legible markings. All to Engineers approval | Item | 1 |  | 0
C1.04 | Sub-total c/f to SWITCHGEAR, EARTHING & CABLING PRICE COLLECTION PAGE |  |  |  | 0
C2 | MAINTAINED POWER AND RISING MAINS
1000A TPN rated with all necessary accessories. To be complete with tap - off units per each floor fixing bolts, nuts etc for proper installation of the rising mains.
C2.01 | Fabricated incomer with 1000A TPN MCCB for rising mains protection isolation to match the Switchgear. The MCCB should be adjustable on a scale of 0.75 to 1 and with adjustable overcurrent settings, having a short circuit breaking capacity of 50KA at 415Vac, 50Hz. The Isolator should also have a set of digital energy multimetre for indication of voltage & current | No. | 1 |  | 0
C2.02 | End Feeder Unit for temination of the cable feed to the busbar | No. | 1 |  | 0
C2.03 | Standard length busbar (3M) with male & female ends and all other ficing accessories | LM | 18 |  | 0
C2.04 | End Closer Unit for temination of the busbar | No. | 1 |  | 0
C2.05 | Vertical expansion units | No. | 1 |  | 0
C2.06 | Vertical Fixing Unit (60mm) | No. | 1 |  | 0
C2.07 | 200A TPN Plug-In Tap-Off Box (IP55 rated) installed at all floors | No. | 10 |  | 0
C2.08 | Fire barrier kit on every floor to match the rising mains as Zucchini S120 Fire barrier kit or equivalent to engineers approval. | Floors | 5 |  | 0
C2.09 | Sum for all fixing accessories including suspension brackets | Item | 1 |  | 0
C2.10 | Sub -Total for MAINTAINED POWER RISING MAINS c/f to RISING MAINS PRICE COLLECTION PAGE |  |  |  | 0
C3 | Systems Earthing (PME) - Protective multiple earthing
Pricing to include earth treatment where required using appropriate compounds such as Bentonite and marconite to achieve stipulated impendance. Under no circumstance should charcoal or common salt be used. NOTE: Manufacturers Proof will be required
C3 | LV ROOMS EARTHING:
C3.01 | EARTH MATT: Supply & Install Earthing Matt for Body Earthing of Switchgear complete with a copper lattice matt measuring 1000mm X 1000mm constructed with copper tapes measuring 25mm X 3mm (total length of each matt will be 15M) adjacent to switchgear rooms. This should be extended to the Concrete inspection chamber with appropriate Cable / CU rod. This shall include treatment Compound as stated above. | No. | 1 |  | 0
C3.02 | EARTH INSPECTION PIT: 300mm x 300mm Concrete Inspection Chamber clearly marked "EARTH" | No. | 1 |  | 0
C3.03 | COPPER BAR: Supply & Install a Earth Potential Copper Bar measuring 600m long X 50mm Wide X 6mm Thick, mounted on insulators in room(s) | No. | 1 |  | 0
C3.04 | PIT - EARTH BAR CONNECTION CABLE: Connect the copper lattice matt through the Inspection Chamber and the Earth potential Copper bar in Equipment room SC CU cable c/w appropriate cable lugs, cable lugs & any other accessories required. Cable size as 120 mm sq PVC SC XLPE CU Cables | LM | 23 |  | 0
C3.05 | EARTH BAR - EQUIPMENT CABLING: Connect the Earth potential Bar and Equipment with SC CU cable c/w appropriate cable lugs, cable lugs & any other accessories required. Cable size as 70mm sq PVC SC XLPE CU Cables | LM | 20 |  | 0
C5 | LIGHTNING PROTECTION EARTHING: |  |  |  | 0
C5.01 | EARTH MATT: Supply & Install Earthing Matt for system complete with a copper lattice matt measuring 1000mm X 1000mm constructed with copper tapes measuring 25mm X 3mm (total length of each matt will be 15M) This should be extended to the earth inspection chamber with appropriate 95mm SC Cable | No. | 2 |  | 0
C5.02 | EARTH INSPECTION PIT: Heavy Gauge (5000Kgs) minimum Earth Inspection pit, with Lockable lid & should be engraved 'EARTH' or with earth Symbol | No. | 2 |  | 0
C5.03 | EARTH ROD: Earth rod - tape clamp type A | N0 | 2 |  | 0
C6 | ACCESSORIES
C6.01 | CABLE TIES: Allow for cable ties at one meter interval along the cable trays and cable ladders above at every 300mm interval. | Item | 1 |  | 0
C6.02 | LABELLING: Labelling of all submains cables at both source & end with permanent Tag labels of Visible Font. All to Engineers approval | Item | 1 |  | 0
C6.03 | Sub-total c/f to SWITCHGEAR, EARTHING & CABLING PRICE COLLECTION PAGE |  |  |  | 0
C7 | LV Distribution Boards Cabling & Accessories
C7.01 | Turret 3 Phase Power distribution board installed outside. Busbar rating: 630A Rating Main Incomer: 2No. 630A Outgoers, 2No. 630A Spareway with powder coated matt finish paint, compartmental type, CRCA metalic Sheet, Indication on front side R, Y, B, ON, OFF, Surge Protector and Trip Earthing provision. All breakers to have Over Current and Earth Fault Protection | No. | 1
C7.02 | Cable to DBs Above: 300mm sq 4-Core PVC SWA PVC XLPE CU Cable | LM | 800
C7.03 | Cable glands for above cables | No. | 8 |  | 0
C7.04 | Cable lugs for for above cables | No. | 32 |  | 0
C7.05 | 16Way 200A TPN Distribution Board to each floor wing | No. | 11 |  | 0
C7.06 | 10A SP MCB | No. | 55 |  | 0
C7.07 | 20A SP MCB | No. | 55 |  | 0
C7.08 | 32A SP MCB | No. | 110 |  | 0
C7.09 | Cable to DBs Above: 70mm sq 4-Core PVC SWA PVC XLPE CU Cable | LM | 55 |  | 0
C7.10 | Cable glands for above cables | No. | 20
C7.11 | Cable lugs for for above cables | No. | 80
C7.12 | Cable to DBs Above: 16mm sq 4-Core PVC SWA PVC XLPE CU Cable | LM | 100 |  | 0
C7.13 | Cable glands for above cables | No. | 20 |  | 0
C7.14 | Cable lugs for for above cables | No. | 80 |  | 0
C7.15 | Cable to Duct: 35mm sq 4C PVC PVC CU Cables. | LM | 80 |  | 0
C7.16 | Cable glands for above cables | No. | 4 |  | 0
C7.17 | Cable lugs for for above cables | No. | 16 |  | 0
C7.18 | Cable to PUMP Panel: 16mm sq PVC PVC CU Cables. | LM | 50 |  | 0
C7.19 | Cable glands for above cables | No. | 2 |  | 0
C7.20 | Cable lugs for for above cables | No. | 8 |  | 0
C7.21 | Cable to DBx: 10mm sq PVC PVC CU Cables. | LM | 50 |  | 0
C7.22 | Cable glands for above cables | No. | 2 |  | 0
C7.23 | Cable lugs for for above cables | No. | 8 |  | 0
C7.24 | CABLE TIES: Allow for cable ties at one meter interval along the cable trays and cable ladders above at every 300mm interval. | Item | 1 |  | 0
C7.25 | LABELLING: Labelling of all submains cables at both source & end with permanent Tag labels of Visible Font. All to Engineers approval | Item | 1 |  | 0
C7.26 | Sub-total c/f to SWITCHGEAR, EARTHING & CABLING PRICE COLLECTION PAGE |  |  |  | 0
C9 | SWITCHGEAR, EARTHING & CABLING PRICE COLLECTION PAGE
ITEM | DESCRIPTION |  |  |  | COST (Kshs)
C9.01 | Switchgear & Meterboards |  |  |  | 0
C9.02 | Rising Mains |  |  |  | 0
C9.03 | Systems Earthing (PME) |  |  |  | 0
C9.04 | LV Distribution Boards Cabling & Accessories |  |  |  | 0
C9.05 | Contigency |  |  |  | 400000
C9.06 | TOTAL EXCLUSIVE OF VAT TO ELECTRICAL PRICE SUMMARY PAGE |  |  |  | 400000